3.1 Calculate from the following information, the maximum amount of water heaters of 1kW each that may be installed according to the regulations:

- 10kVa/220 v single phase transformer using a power factor of 0.95

- Floor area 301m²

- Two 0.75kW single phase motors

- One electric oil heater of 500w

- 20 lights

3.2 Test your answer by making use of any other alternative method.

KVA = KW x PF = 10000 x 0.95 = 9500

Floor area is 301 thus 	0-100 = 	5KW

100-200=	1

200-300=	1

300-400= 	1 remember 1KW for each square or part of a 100 square

Thus 8 KW

Always do the calculation in a table format and in watts because otherwise you can easily confuse yourself

|  | Connected load | Diversity factor | Estimated load |
| --- | --- | --- | --- |
| SSO (switch socket outlets) | 8000 | 50% | 4000 |
| 2x .75kw motors = 750x2 | 1500 | 100% | 1500 |
| 1x oil heater | 500 | 50% | 250 |
| 20 lights x 60W ea | 1200 | 50% | 600 |
| ToTAL | 11200 |  | 6350 |

Transformer output 9500 – 6350 = 3150 watt still available

Now you can either redo the table method or do the amp calculations

|  | Connected load | Diversity factor | Estimated load |
| --- | --- | --- | --- |
| SSO (switch socket outlets) | 8000 | 50% | 4000 |
| 2x .75kw motors = 750x2 | 1500 | 100% | 1500 |
| 1x oil heater | 500 | 50% | 250 |
| 20 lights x 60W ea | 1200 | 50% | 600 |
| 3x1Kw geysers | 3000 | 100% | 3000 |
| ToTAL | 14200 |  | 9350 |

Which is less than the transformer max load thus acceptable

9500 / 220 = 	43.18A FLC (full load current) which we must not exceed

6350 / 220 = 	28.86 amp load

14.316 A spare

1 x gey = 1000 / 220 = 4.545A for each heater

14.316 / 4.545 = 3.15 but you don’t get half a geyser thus 3 geysers can be added

6350 + 3000 = 9350 / 220 = 42.5 amp because a circuit breaker is design and manufactured with 125% of the rated current a 40A circuit breaker can be used for the main switch.

Student wrong methods used below

3.1 answer:

Total load :

- Socket outlets -Floor area 301 m² = (5 kw for first 100 m²) + (1kw for second 100m²) +( 1kw for part of third 100m²)  TOTAL = 7kw x diversity of .5 = 3.5kw

- Motors = (.75kW x 2 ) = 1.5kW x diversity factor of 1 =1.5kW

- Electric oil heater = 0.5kW x diversity of .5 = .25kW

- 20 lights ( 20 x 60watts ) = 1200watts = 1.2kw x diversity of .5 = .6kW

- TOTAL LOAD ( 3.5kW+1.5kW+0.25kW+.6kW) = 5.85kW

Therefore total current required = 5.85kW / 220v = 5850 /220 = 26.6A

Max supply from transformer at full load (10000 *.95) /220 = 43.18 amps.

43.18 max load 8 90% = 38.86amps allowable.

Therefore remaining amperage is 38.86-26.6 = 12.26Amps.

Each heater requires: 1kw

Therefore amps required per is 1kw/220 1000/220= 4.54 amps x diversity factor of 1 = 4.54 Amps.

Therefore total amount of water heaters allowed is 12.26amps/4.54 amps = 2.7.

To check total load with two connected : 26.6amps + (4.54 x 2) = 35.68

To check total load with three connected 26.6amps + (4.53 x 3) = 40.19

Therefore to enable the transformer to be loaded at 90% max only two may be added.